## Slide 1
Motor Operator for VFI Switchgear
University of Pittsburgh: Theodore Beyene, Samuel Bucior, Jason Carney, Arthur Eichelberger
Eaton:
John Guldan

## Slide 2
Vacuum Fault Interrupter (VFI) Switchgear
Public domain
Background
Public domain
Public domain
=

## Slide 3
How it works:
Powerful springs are tensioned, storing energy.
The springs open the circuit extremely quickly.
Tensioning the springs requires high torque (up to 60ft-lb).
Public domain
Background
Left: Slow motion “tripped” response

## Slide 4
Original design: $1000
Last year’s design: $450
Final Goal: Under $400
Background
Goal: Use an actuator rather than a person to flip the switchgear

## Slide 5
Requirements
Provide 60ft-lb of torque
Operate on 24V input
Minimum speed of 4 RPM
Less than 2° overtravel
Under $400
Minimum Requirements
  Manual operation without the use of a pin
  Use the original handle
  Within 4” of all sides of switchgear case
  Configurable to work with multiple angles of travel
Stretch Goals

## Slide 6
Planning: Electronics
Old: Limit switch
Hall effect
Est. price | $50 | $10 | $10
Lifetime | Great | Infinite | Good
Setup | Manual | By design | Either
Compatibility | Either | Two designs | Either
Potentiometer

## Slide 7
Planning: Motor Selection
Cheap: $80
Integrated gearbox
Already part of supply chain
Linear actuator assembly: $1000

## Slide 8
Planning: Shaft driving
Integrated gearbox
High torque to backdrive
4 Bar Linkage
Cheap to manufacture
Difficult to model torque and speed w.r.t. angle
Sprocket and Chain
Torque from motor and user increased by constant ratio
Cheap, but harder to install
Integrated gearbox
High torque to backdrive
4 Bar Linkage
Cheap to manufacture
Difficult to model torque and speed w.r.t. angle
Sprocket and Chain
Torque from motor and user increased by constant ratio
Cheap, but harder to install

## Slide 9
Planning: Sprockets
ANSI 40 Heavy Duty
  Expected force:
    F=T/Rsprocket
    720in-lb/1.65in =424lbf
    Capable of 4000lbf
  Reduction:
    11T and 19T
    Max torque at motor decreased to 35ft-lb
    Speed decrease

## Slide 10
Testing: Motor

## Slide 11
Testing: Motor Analysis
Chart: Voltage vs Stall current and Stall torque
| 3 | 4.5 | 6 | 7.5 | 9 | 12 | 15
Torque (ft-lb) | 15 | 21 | 28 | 35 | 45 | 58 | 72
Current (A) | 3.2 | 5.2 | 6.5 | 8.1 | 10 | 13.1 | 15.5

## Slide 12
Testing: Motor Analysis
Chart: Motor Characteristic Curves at 24V

## Slide 13
Testing: Demo potentiometer

## Slide 14
Building: Electronics - PCB Design

## Slide 15
Building: First Mockup

## Slide 16
Building: Final Product

## Slide 17
  Manual operation without the use of a pin
  Use the same handle
  Within 4” of all sides of switchgear case
  Configurable to work with multiple angles of travel
  Work on both sides
Conclusion
  Provide 60ft-lb of torque
  Operate on 24V input
  Minimum speed of 4 RPM
  Less than 2° overtravel
  Under $400
Stretch Goals
Minimum Requirements
90ft-lb
18-30V
6.3RPM
Testing
$350 for 20+
Reduced to 45ft-lb
Breaker bar
<3.5”
4°-296°
Mirror

## Slide 18
Acknowledgements
John Guldan
Switchgear Engineer at Eaton
Contact at Eaton, always available
Thorin Tobiassen and Andy Holmes
Swanson Center for Product Innovation (SCPI)
Design/manufacturing consulting
Josh Brown
Electrical Engineer at Human Engineering Research Laboratories (HERL)
Mentor for general circuit and PCB design
Dr. Stephen Ludwick
Professor at Pitt
Director of Advanced Technology at Aerotech
Initial design brainstorming

## Slide 19
Questions?
???